SmartPowerMonitor Software Design

# Introduction
## Meridian Smart Power Meter Information
LED flashes code for the Kwh usage.
1600 flashes equates to 1KWh, I.e a load of 1KW for a period of 1 hour.
Thus an instantaneous load of 1KW will cause a flash rate of 1600/3600 = 0.444/sec, or 1 flash every 2.25 seconds.
The optical sensor interface hardware schematic is shown below:

## Timer Requirements
Peak instantaneous expected loads might be of the order of say 15 to 20KW. The pulse rate would be (15, 20) x 0.444 = (6.66,8.88) flashes/sec. A load change of 100W would change the flash rate by 0.044/sec. I.e the time between rising edges of a pulse from the optical detector would change from (for 20KW) 112.5ms to (8.933Hz) 111.94ms, a delta of 0.56ms.
At the other end of the scale, a minimal load, or a change in load of 100W would be responsible for a flash rate of 0.1 x 1600 = 160 flashes/hour, or 1 flash every 22.5 seconds, or 0.044/sec. So, if load was 1KW and changed to 1.1KW then pulse rate goes from 0.4444/sec, or time between rising edges of pulse output from optical detector 2250ms to 0.48888/sec or 2045.45ms, a delta of 204.5ms.
Minimum resolution requirements for on board time measurement of the pulses are driven by the instantaneous load measurement resolution required at high loadings. The dynamic range of the on board timing is dictated by the lowest total loading we wish to be able to measure. If we only want to be able to measure down to 1KW then a timer range of around 2.25 seconds would be sufficient. A 5 second duration measurement capability means we can measure down to 0.5KW.
Using only the on board ATTiny2313 timers, without resorting to software range extension, the 16 bit timer (timer1) clocked with a pre-scaler of 1024 and an F_CPU = 3686400Hz gives a tick rate of 3600/sec. The dynamic range of the 16 bit counter (uint16_t) is 65535, rolling over to 0 at the next increment, thus rollover after every 65536 intervals or (65536/3600) = 18.204444 seconds. A measurement interval capability of 18 seconds would correspond to a minimum instantaneous load measurement capability of 1000W/(1600*(18/3600)) = 125W.
# High Level Architecture
Primary components to the power meter monitor
PC software for querying the data logger receiver module and storing the resulting information to an appropriate database. Also for generating dynamic web page with graphs of current and historical data. Software may be written in Python.
- Optical detector to convert Smart Meter's LED pulses to digital pulse train, to be used as external interrupt input to the Power Meter Monitor remote sensor node (Hardware)
- Power Meter Monitor remote sensor node (based around ATMega328P) interfaced to optical detector conditioning circuit, and to a 434MHz RF transmitter to transmit pulse measurements at regular intervals. This node will handle pulse duration measurement, pulse counting, and keep some non volatile
- Intelligent Receiver data logger module (hardware + software)
  - 434MHz receiver module for receiving remote sensor measurements.
  - Convert pulse count and rate measurements to KW, KWh etc
  - Real time clock, time stamping of power meter samples
  - Data memory archiver -logging power meter samples to non-volatile memory and providing the capability for querying/downloading specified ranges of data by external client applications, via comms interface.
  - Uart comms routines to allow external applicatons (host PC) to configure various power meter monitor parameters, and to allow downloading of archived power meter samples from archive memory.
# Interrupts
The output of the photodetector circuit will consist of a TTL pulse train. This will be connected to one of the external interrupt GPIO pins of the microcontroller. In the case of the AT90S8515 either INT0 (PD2, pin 12) or INT1 (PD3, pin 13) can be used.
The interrupt service routine will be responsible for keeping track of the length of time that has passed between pulse edges, and the cumulative number of pulses that have occurred within some given time period. This in turn can be directly related to instantaneous power load and total Kwh usage.

The interrupt vectors are defined in the specific device io header file. This include is not added directly to a project but the project settings will ensure the correct header is included indirectly via the <avr/io.h> header.
e.g For the 8515 device
/* External Interrupt Request 0 */
#define INT0_vect	_VECTOR(1)
#define SIG_INTERRUPT0	_VECTOR(1)

/* External Interrupt Request 1 */
#define INT1_vect	_VECTOR(2)
#define SIG_INTERRUPT1	_VECTOR(2)

Timer Interrupt

TCCR1B |= (1 << CS10); // Set up timer, clock select, lower 3 bits determine clock source (internal/external) and also the prescaler value.

// Set up timer 1, 16 bit timer, use prescaler of 1024
TCCR1B |= (1 << CS12) | (0 << CS11) | (1 << CS10);

Prescaler Value | Resolution @ 1MHz
              1 |  1uS
              8 |  8uS
             64 | 64uS
            256 | 256uS
           1024 | 1024uS

With a maximum count of 65535 before rolling over this gives maximum measurable intervals of

Prescaler Value	Resolution@8MHz	Maximum Interval, sec
1	0.125uS	0.008192
8	1uS	0.065536
64	8uS	0.524288
256	32uS	2.097152
1024	128uS	8.388608

We really need to be able to time pulse events that are potentially greater than 30 seconds apart at their maximum (very low power use). This is an extreme and is unlikely to occur in practice. However, if we are to accommodate long intervals we will need to software extend the timer and keep track of the number of 16 bit timer1 overflows.

A more realistic scenario is that we will want to be able to distinguish the difference between an instantaneous load of 2.5KW and 2.6KW. This load causes a change in duration between pulses of:
2.5KW = 2.5 x 1600/3600 = 1.11 pulses/sec or 900ms between pulses
2.6KW = 2.6 x 1600/3600 = 1.155 pulse/sec or 865.4ms between pulses.
So, we can get the power resolution without recourse to a software extended timer, however the minimum instantaneous power load we could measure would be:
(1/8.388) = 0.119 pulse/sec => 0.119 x 3600 = 428.4 pulse/hour
(428.4/1600) = 0.268KW

# Load Calculations
To calculate an instantaneous load figure we could work backwards from our duration between pulses. For example, let the last time measured between rising edge of pulse detector be 256.3ms. Calculate how many pulses that would equate to per hour:
3600 x 1000 milliseconds/256.3, or rather, to avoid decimal fractions, multiply top and bottom by 10,
pulses_per_hr = 36000000/2563 = 14046
Now we know that 1600 pulses in a 1 hour period corresponds to 1KW load for 1 hour, thus 14046 pulses per hour is equivalent to an instantaneous load of (14046/1600) = 8.78KW. We need to avoid decimal fractions so we should use a constant of 3600 (sec) x 100000 (0.01ms) for the numerator. The calculation becomes:
pulses_per_hr x 10 = (360e6) / (10 x pulse_interval_ms)
pulses_per_hr x 10 = 140460

kw_load x 10 = (pulses_per_hr x 10) / 1600
kw_load x 10 = 140460/1600 = 88 (rounding up), which means 8.8KW

Averaging
Of course we could do some averaging of our pulse intervals to get a 'smoother' result. We could select to average over a specific number of pulse events, say 10. We would need to keep a record (array) of the last pulse interval times. These could be kept in units of timer ticks rather than converting each one to ms before averaging. The conversion to ms can be done after the averaging